Notes 10: Conductor sizing & an example

10.0 Conductor sizing

Since it is impractical to manufacture an infinite number of wire gauges, standards have been adopted for an orderly and simple arrangement of such sizes.

The American Wire Gauge (AWG) sizes conductors, ranging from a minimum of no. 40 to a maximum of no. 4/0 (which is the same as “0000”) for solid (single wire) type conductors. The smaller the gauge number, the larger the conductor diameter.

For conductor sizes above 4/0, sizes are given in MCM (thousands of circular mil) or just cmils.

What is a cmil? A cmil is a unit of measure for area and corresponds to the area of a circle having a diameter of 1 mil, where       1 mil=10-3 inches.

The area of such a circle is πr2= π(d/2)2, or

π(10-3/2)2=7.854x10-7 inches2

1 kmil=1 inch.

1 cmil=(1 mil)2 and so corresponds to a conductor having diameter of 1 mil=10-3 in.

1000kcmil=(1000 mils)2 and so corresponds to a conductor having diameter of 1000 mils=1 in.

To determine diameter of conductor in inches, take square root of cmils and then divide by 103:

Diameter in inches=.

Stranded conductors (multiple strands of wire) for distribution purposes usually range from a minimum of no. 6 to a maximum of 1,000,000 cmil.

It is quite common to specify conductors in terms of the size (or gauge), the strands, and the layers. For example, 4/0 6/1 indicates AWG size 0000, with 6 strands and 1 layer.

The table below shows conductor sizes commonly used in distribution systems.

10.1 Example

Determine the phase impedance matrix [Zabc] and the sequence impedance matrix [Z012] in Ω/mile for the 3-phase pole configuration shown in Fig. 1. The phase and neutral conductors are 250,000 all-aluminum.

Fig. 1

From the table of conductor data, we see that for 250,000 cmil AA conductor, the diameter is 0.567 inches, the GMR is 0.0171 ft, and the resistance is 0.41Ω/mile.

From eqs. (39,40) of Notes 9, we have:

With f=60 and ρ=100, these equations are:

So we need to compute the self terms for the four conductors (which will all be the same since they all have the same GMR). We also need to compute the mutuals, which will be the harder part because we need to obtain a mutual for each pairwise combination. This is 4 things taken 2 at a time, which is

4!/2!(4-2)!=6.

So we have 6 calculations to make.

First, lets do the self term, since it is easiest.

To get the mutuals, we need to determine the distance between conductors.

a to b: sqrt(42+22)=4.4721

a to c: 2+2=4

a to n: sqrt(42+62)=7.2111

b to c: sqrt(42+22)=4.4721. Same as a to b.

b to n: 2+2=4. Same as a to c.

c to n: sqrt(42+22)=4.4721. Same as a to b.

Therefore, the primitive impedance matrix is

The abc matrix is then found by Kron reduction based on the formula we developed:

where we define:

In our problem, the necessary matrices are:

Plugging in to get Zabc, we obtain

We will refer to Zabc as the phase impedance matrix. Note carefully that the self terms are all different, and there are three different mutual terms. This is because of the difference in their positions relative to each other and relative to the neutral conductor and the fact that there is no transposition. However, the matrix is symmetric, i.e., what the a phase sees looking at b-phase is the same that b-phase sees looking at a-phase.

Now let’s compute the sequence matrix Z012.

This is given by Z012=A-1ZabcA, which is

where

and

resulting in

Clearly the sequence networks are not decoupled. Important point to be made here is that, because sequence networks are not decoupled, they offer no real advantage over the abc network in terms of analysis.

10.2 Two phase and single phase lines

If one is given a single phase or two phase configuration, with or without neutrals, then one may apply the same procedure as for the 3-phase configuration, i.e.,

- Determine resistance per mile and GMR of each conductor.

- Determine distance between conductors.

- Compute primitive impedance matrix using eqs. (39,40) of notes 9 with appropriate value of resistivity ρ.

- Perform Kron reduction to eliminate the presence of the neutral and thus obtain the phase impedance matrix.

Notes:

- The primitive impedance matrix of step 3 will be square with dimension equal to the number of conductors that you have in the configuration.

- The phase impedance matrix of step 4 will be square with dimension equal to the number of phase conductors that you have in the configuration.

So a single phase configuration, with neutral, will result in a 2x2 primitive impedance matrix and a 1x1 phase impedance matrix.

If by chance a single or two-phase configuration extends from a three phase configuration without changing the positions of the remaining conductors, then one may just pull out the appropriate elements from the 3x3 phase impedance matrix corresponding to the 3 phase configuration.

For example, if

is the phase impedance matrix for the 3 phase configuration, if we run a 2-phase lateral using phases a & c without changing the a & c phase & the neutral position, then

Likewise, if we run a single phase lateral using phase b with without changing the phase b position relative to the neutral, then

If positions do change, then non-0 elements of above matrices will need to be recomputed. However, we will be able to use 3x3 matrices for any line configuration.