Notes 11: Cables

11.0 Introduction

Underground conductors are more expensive than overhead conductors because the entire length of each conductor must be insulated

- from the ground and

- from other conductors

Therefore, cables are generally used for underground distribution. The most salient difference between cables and overhead conductors is that cables are insulated.

In addition, to obtain a given ampacity, a cable requires a larger conductor than an overhead line because cables do not dissipate heat well because of 2 reasons:

- No wind

- Insulation confines the heat

This further increases cable cost compared to overhead.

And that is just for the wire. In addition, cable installation is more costly than overhead installation because of the variability of soil conditions. If the job requires trenching through the rich soil of Iowa farmland, installation cost is generally slightly higher. But if even in a relatively short distance of the overall installation, the soil is very rocky, or worse yet, underneath concrete or asphalt, costs can skyrocket.

Some 1991 data indicates single-phase cable installation are 1.3 to 2.4 times the cost of equivalent overhead, whereas three-phase cable installation is 1.7-7.6 times the cost of overhead [1].

So what are the reasons for going underground? There are 4 main reasons:

- Aesthetics: Only power engineers really like to look at overhead lines (.

- Safety: Overhead is exposed and can fall. Other strange things can happen as well. Underground is not exposed.

- Reliability: Overhead circuits typically fault about 90 times/100 miles/year. In contrast, underground faults less than 10 times/100 miles/year [1].

- Maintenance: The number 1 maintenance cost for overhead, tree-trimming, is entirely eliminated with underground.

- Reach: With greater diameters to obtain desirable ampacity, reactance is decreased and therefore voltage drop is lower.

11.1 Cable construction

There are seven distinguishing features in regards to cable construction.

- Single phase vs. polyphase

- Neutral

- Conductor

- Insulation

- Shielding

- Jackets

- Burial

11.1.1 Single phase vs. polyphase

Cables may have 1, 2, 3, or 4 conductors. Use of multiple conductors saves money, as only 1 shield and 1 jacket is necessary and they are easier to install.

Single phase conductors are used when the cable is to be tapped frequently, as is the case for street lighting and for underground residential distribution (URD). In fact, it is common now to refer to single phase cable as URD cable.

11.1.2 Neutral

The neutral may be non-concentric or concentric.

The non-concentric neutral typically has only a single neutral wire. Fig. 2 above shows such a configuration, which is shown in Fig. 3 in cross-section.

Fig. 3

Concentric neutrals, on the other hand, have neutral wires wound helically around the insulation shield, as shown in Fig. 4 below.

Fig. 4 [1]

URD (single phase cable) almost always uses the concentric neutral configuration. It may also be used in 3-phase cables where each cable then carries its own neutral. It is in this case that we see the six conductor configuration previous mentioned (see eq. 42 of “Notes 9”).

In fact, it is possible to have a 7-conductor configuration, which is the 3-phase case with concentric neutrals together with a separate neutral conductor.

Neutrals can be designed to have the same resistance as the phase conductor, in which case they are referred to as “full neutrals” in that they are designed to carry the same current as the phase. URD cables typically have full neutrals.

Neutrals can also be designed to have greater resistance than the phase conductor and therefore be capable of carrying 1/3 of the phase current. The “one-third” neutral is common with three-phase cables.

A last type of neutral is used in tape shielded cables. This type of cable consists of a central phase conductor covered by a thin layer of nonmetallic semiconducting screen to which is bonded the insulating material. The insulation is covered by a semiconducting insulation screen. The shield is bare copper tape helically applied around the insulation screen. An insulating jacket encircles the tape shield. Fig. 5 below illustrates a tape-shielded neutral cable.

Fig. 5

11.1.3 Conductors

Conductors may be copper or aluminum. Copper is a slightly better conductor than aluminum (lower resistivity) and therefore the same ampacity can be achieved with a lower diameter cable. However, aluminum is lighter and less expensive. As a result, aluminum is most common.

The conductor will normally be stranded in order to increase its mechanical flexibility.

Note: ACSR is never used in underground cables. Why not?

11.1.4 Types of insulation

Insulation is critical to the cable because of three main reasons.

- Insulation must (obviously) provide sufficient insulation between the conductors. This means it must have a dielectric breakdown higher than the voltage gradient between the phases. For example, a 0.175 in thick polymer cable is designed to insulate against 8 kV, which is a 46 kV per inch gradient.

- Insulation must withstand high temperatures during high loading.

- Insulation must provide physical protection against any kind of mistreatment that might ever occur 4 feet underground (moisture, rodents, digging).

There are three basic types of cable insulation in use today.

- Paper: These are sometimes referred to as paper-insulated lead-covered (PILC) cables. The paper is impregnated with insulating oil which increases the dielectric breakdown voltage of the paper. A lead sheath is used to keep the moisture out and the oil in.  PILC failures are due to moisture ingress, oil loss, or thermal stress. PILC was the first type of cable used and, although it is rarely used in new installations, there are many such cables still in operation.

- Plastic compounds: The most common of these is polyethylene (PE). It is cheap, strong, and has good insulation strength.

- Rubber or rubber-like compounds: There are several of these, as follows:

  - Crosslink polyethylene (XLPE).

  - Ethylene propylene rubber (EPR).

  - Isobutylene isoprene (Butyl).

  - Styrene butadrene rubber (SBR).

These have excellent electrical and physical insulation properties and can be used in up to 138 kV applications. EPR in particular is good for submarine crossings.

11.1.5 Shielding

The shield is a conducting layer surrounding another part of the cable. There is normally a shield surrounding the conductor (a conductor shield) and a shield surrounding the insulation (an insulation shield).

These shields serve the important function of reducing sharp “edges” associated with the physical construction of the cable. Such edges, which occur on “seams” or “boundaries” between different parts of the cable, such as:

- between conductor and insulation

- between insulation and jacket

represent a sharp change in dielectric and as a result, create very high voltage gradients. The shields serve to reduce these high voltage gradients.

The insulation shield also serves the function of confining the electric field of the cable to the insulation surrounding the conductor. This is because it represents the other “plate” of a parallel plate capacitor and will therefore have charge on it equal and opposite to the charge on the conductor. Recalling Gauss’ law for electric fields, which says the net outward electrostatic flux through any closed volume is equal to the charge enclosed by that volume, we see that the net outward electrostatic flux outside the insulation must be zero.

The confinement of the electric field tends to minimize interference with communication media that might be close to the cable.

All cables above 8kV must be shielded to satisfy NEC. Cables below 2 kV are usually not shielded. Between 2 and 8 kV, it may or may not be shielded.

11.1.7 Jackets

The jacket is also referred to as the armor, and like this latter name suggests, its function is to provide physical protection from environmental and installation conditions.

The jackets may be nonmetallic or metallic.

Nonmetallic jackets are usually PVC, PE, or XPLE.

Metallic jackets are interlocker armor, corrugated metal, lead, aluminum, or copper.

11.1.8 Burial

Cables placed underground in 1 of 3 ways:

-direct burial

-ducts or pipes inside concrete sheaths

-tunnels built for other reasons: sewer, water

11.2 Data

The tables provide typical cable data.

References

[1] T. Short, “Electric power distribution handbook,” CRC press, 2004.

[2] www.mysouthwire.com/Southwire/cda/front_door/0,1256,,00.html

# Footnotes

The term semiconducting, as used here, means “somewhat conducting” in that the material has some resistance, more than the conductor but less than the insulation. The term “semiconducting,” as used here, does NOT refer to nonlinear resistive materials like silicon or metal oxide. Here, the resistance is fixed and does not change with voltage.