Notes 16: Voltage Regulation2

Single phase step voltage regulators

16.0 Configuration and basic operation

As a result of our conclusion in “Notes15” that the pu impedance of an autotransformer is quite small, we will neglect it in the analysis contained in these notes.

Step voltage regulators have both single phase and 3 phase applications. We focus in these notes on the single phase applications.

There are two broad classes of single phase step voltage regulators, referred to as Type A and Type B. They differ in whether the

- (Type A) source voltage is to be applied across one winding (and load voltage taken across both windings) or

- (Type B) source voltage is to be applied across both windings (and load voltage taken across one winding).

Figure 1 shows a type A step-up voltage regulator. The diagram on the right is a simplification of the diagram on the left.

Fig. 1: Type A boost configuration

Figure 2 shows a type A step-down voltage regulator. Note the position of the switch inside the dotted circle in Figs. 1 and 2.

Fig. 2: Type A buck configuration

Figure 3 shows a type B step-up voltage regulator. The diagram on the right is a simplification of the diagram on the left.

Fig. 3: Type B boost configuration

Figure 4 shows a type B step-down voltage regulator. Note the position of the switch inside the dotted circle in Figs. 1 and 2.

Fig. 4: Type B buck configuration

Some things to note about Fig. 1-4…

The notation S is “source,” L is “load,” and SL is “source-load” which indicates to what the respective terminal is connected.

The switch inside the dotted circle is called a reversing switch. This switch toggles the regulator between the boost and buck configurations.

The upper winding in each figure has the taps. The taps enable changing the number of turns for the indicated winding and in doing so provide adjustment to the turns ratio and therefore the load voltage.

The preventive autotransformer, shown in each figure between a terminal and the taps, has the function of preventing the regulator from being disconnected from the circuit each time the tap is changed.

A more detailed diagram is shown for the preventive transformer and associated components in Fig. 5.

Fig. 5: [1]

In Fig. 5, one observes the preventive autotransformer, the transfer switches, and the selector switches.

Without the preventive autotransformer and the transfer switches, when making a tap change, if opening selector switch j occurs before the closing of selector switch j+1, the main line through the regulator will open circuit.

We can see how this is avoided by discussing the case of moving from tap position 1 to tap position 2.

When the tap is in position 1, transfer switch A is closed, B is open, and C is closed. All selector switches are open except 1. Fig. 6.

When switching to position 2, the transfer switches A and B close, C opens, and selector switches 1 and 2 are closed. Fig. 7.

When the tap is in position 2, transfer switch B is closed, A is open, and C is closed. All selector switches are open except 2. Fig. 8.

Since Figs. 6 and 8 represent steady-state configuration and Fig. 7 represents the switching configuration, we see that at no time is it possible to encounter an open circuit.

The preventive autotransformer is required in order to smoothen the transient encountered when switching from the Fig. 6 configuration to the Fig. 7 configuration, since there will be, initially, a voltage difference between the tap 1 and tap 2 position.

The preventive transformer provides a low impedance path to the load current since the two sides are effectively in parallel. But it provides a high impedance path to circulating currents encountered in the Fig. 7 configuration, since the two sides are in series. This is good because we desire minimum impedance to load currents and maximum impedance to circulating currents.

Table 1 provides the sequence of operation of full operation from taps 1 to 9.

Table 1 [1]

Additional explanation of regulator operation can be found in [2].

16.1 Regulator rating

Step voltage regulators differ from standard autotransformers in that they are rated on the 2-winding transformer basis rather than the autotransformer basis.

This means step voltage regulators are rated on the kVA transformed rather than the kVA passed through.

Recall Fig. 3, repeated here for convenience:

Fig. 3: Type B boost configuration

Example 1:

Assume we need 1000 kVA of flow-through capacity. What should be the capacity of the regulator if the turns ratio is nt=N2/N1=1/11?

The input voltage is

The autotransformer will need to carry

With Sauto=1000 kVA, then we need:

Thus we see that the iron and windings required for the regulator need be able to handle only 10% of the flow-through of the circuit it is regulating.

But what will be the voltage transformation in this case?

So we see that we obtain a 10% voltage boost in this case.

16.2 Voltage and current equations

The defining voltage and current equations for the Type B step-voltage regulator in the raise (boost) position are developed in Table 1, resulting in eqs. (6) and (7).

Table 1: Type B – Boost Position

| Voltage equations | Current equations |  |
| --- | --- | --- |
|  |  | (1) |
|  |  | (2) |
|  |  | (3) |
|  |  | (4) |
|  |  | (5) |
|  |  | (6) |
|  | (7) |

The defining voltage and current equations for the Type B step-voltage regulator in the lower (buck) position are are developed in Table 2, resulting in eqs. (13) and (14).

Table 2: Type B – Buck Position

| Voltage equations | Current equations |  |
| --- | --- | --- |
|  |  | (8) |
|  |  | (9) |
|  |  | (10) |
|  |  | (11) |
|  |  | (12) |
|  |  | (13) |
|  | (14) |

In comparing the final equations for the boost configuration of Table 1, eqs. (6) and (7), with the final equations for the buck configuration of Table 2, eqs. (13) and (14), we see that the only difference between them is the sign of the turns ratio per eqs. (7) and (14).

16.3 Regulator ratio

The parameter aR in eqs. (7) and (14) is called the regulator ratio. Typical maximum boosts and bucks are ±10%. What will aR and nt=N2/N1 be in the maximum boost and buck positions?

Maximum boost position:

Consider eq. (6):

( (

Then from eq. (7),

(

This is a ratio of 1/11, which was the ratio used in example 1.

Maximum buck position:

Consider eq. (13) (same as eq. (6)):

( (

Then from eq. (14),

(

This is a ratio of 1/9.

16.4 Voltage regulation per step

Most regulators today will have 32 steps for ±10% regulation, with 16 steps in either direction.

Since 16 steps provides 10% boost (or buck), then a single step will result in a voltage change of 1/16 of 10%, which is:

or 5/8% per step.

Since “% voltage” is “pu voltage” x 100, the pu voltage change per step is

So we obtain 0.00625 pu voltage change per step.

16.5 Regulator ratio from tap

We have previously used the term “tap position” to denote the position on the tapped winding of the tapping terminal.

It is common to use the term “Tap” to refer to the numerical identity of the position on the tapped winding if the tapping terminal. Therefore, the range of Tap is from 1 to 16.

Note that information characterizing a regulator will not include the effective ratio (N2/N1)effective corresponding to each tap position. Normally, you will have only the numerical identity of the tap position, Tap. The ratio (N2/N1)effective is then given by the pu voltage change per step times the number of steps (Tap):

(15)

Note that if Tap is 0, then the effective turns ratio is 0. In this case, there is no boost, and VL=VS.

For the boost configuration, we recall eq. (7), repeated here for convenience:

(7)

Substituting eq. (15) yields:

(16)

Likewise, for the buck configuration, we get

(17)

16.6 abcd model

Repeating eqs. (6) and (13) here,

So the abcd model would be as follows:

(19)

(20)

where

(21)

(22)

(23)

(24)

16.6 Control

The tap changing is controlled by a

- line drop compensator actuating a

- voltage relay with time delay which drives

- motor operating circuit controling a motor to push up and down the taps as needed

A conceptual (block) diagram of the control process is shown in Fig. 9 where the LDC receives inputs proportional to (a) voltage across and (b) current through the feeder being regulated.

Fig. 9

We will describe each of the main blocks shown in Fig. 9.

16.4 Line drop compensation operation

Without line drop compensation (LDC), a voltage regulator will control the voltage at its own location. However, it is typical that we desire to control the voltage at a location downstream from the voltage regulator, i.e., at the far-end of the feeder.

Fig. 10 shows a detailed diagram of an LDC.

Fig. 10: Line drop compensator circuit

Some items to note in regards to Fig. 10:

- Choose the potential transformer (PT) to give a 120 v nominal voltage on the relay side. So when substation low side voltage is kVlow (rated voltage), Vreg=120. Thus, if we choose the line-to-neutral voltage kVlow as base voltage on feeder side, then 120 is base voltage on relay side. In per-unit, Vsend=Vreg.

- Because the isolation transformer between relay side and LDC side is 1:1, the voltage base on the LDC side is also 120.

- The voltage relay draws no current, it only monitors voltage. Therefore, the current through the isolation transformer is zero.

- Choose the current transformer (CT) to have current rating of CTp:CTs, where CTp is usually chosen as rated feeder current.

- The drop across the 1:1 isolation transformer, Vdrop, equals the drop across the LDC impedance R+jX.

- If R and X are chosen so that they are, in per-unit, equal to Rline+jXline in per-unit, then (Vsend-Vload)=Vdrop.

Solve the last relation for Vload, we have, in per-unit,

Vload=Vsend-Vdrop						(25)

Note from the relay circuit that

Vrelay=Vreg-Vdrop						(26)

However, in per-unit, Vsend=Vreg.

From (25) and (26), we conclude that, in per-unit, Vrelay=Vload  !!!

Even better, since the relay circuit voltage base is 120, Vrelay gives the actual service voltage (at the meter) seen by the load.

Because we want to maintain load voltage between 114 and 126, we could set the voltage relay to actuate when it sees voltage drop below 120 v.

Now how to design the circuit to make this happen? By “design the circuit,” we mean we need to choose appropriate values of LDC resistance R and reactance X.

16.5 LDC Design

Key to LDC design is choosing a consistent set of bases for the per-unitization. You must do this correctly. Table 3 summarizes this consistent set of bases.

Table 3: Base Quantities

| Base quantity | Feeder side | Relay & LDC side |
| --- | --- | --- |
| Voltage | VLN,rated=kVlow | 120 |
| Current | CTp | CTs |
| Impedance | Zbase,L=VLN,rated/CTp | 120/CTs |

In what follows, we will assume that we know the feeder impedance, and it is denoted in ohms as RlineΩ+jXlineΩ.

The per unit value of the (feeder and LDC) impedance is given by

(27)

With Zbase,L as given in Table 3, eq. (27) is:

(28)

Now we want the ohmic value of the compensator impedance. This is obtained by multiplying the per-unit value by the LDC-side impedance base given in Table 3, as in eq. (29).

(29)

One interesting issue is that LDC impedance settings are typically dialed in as a voltage, and the dialed in voltage is the voltage, in volts, seen across each impedance element when rated current is flowing.

To obtain the voltage settings corresponding to the ohmic values of R and X given in equation (29), we need to multiply by CTs. We denote the corresponding LDC settings using primed notation, i.e.,

(30)

Example 2:

A substation transformer is rated 5000 kVA, 115kV:4.16kV, and the equivalent line impedance from the regulator to the load center is 0.3+j0.9 ohms.

- Determine the voltage transformer and current transformer ratings for the compensator circuit.

- Determine the R and X settings of the compensator in ohms and volts.

Assume that the phases are balanced, and you are designing the regulator for a single one of the phases.

Solution:

- PT and CT settings:

PT setting:

The rated line-to-ground voltage of the substation transformer is 4160/sqrt(3)=2401.8 volts.

To obtain 120 volts in the relay circuit, we need a PT with a turns ratio of 2401.8:120=20.015.

CT setting:

The rated current in the feeder is obtained based on |S3|=sqrt(3)|V||I|( |I|=|S3|/(sqrt(3)|V|), i.e.,

The primary rating of the CT on the feeder side is selected to be 700 A. To work with reasonably small current levels in the LDC circuit, we will choose a CT ratio to give us a rated LDC-side current of CTs=5 A. Therefore the CT ratio is

CTp/CTs=700/5=140

2. R and X settings:

Applying eq. (29), we obtain the ohmic value of the compensator impedance as:

And we obtain the voltage settings by multiplying by CTs:

16.6 Obtaining equivalent line impedance

In Example 2, the ohmic value of the line impedance was given. If the feeder radially feeds a single load at the end of the feeder, this impedance is the actual impedance of the single phase line between the point of regulation and the load.

However, if there are multiple taps along the line, then the current at the sending end does not flow all the way to the load.

In this case, we use an equivalent impedance computed as if the sending end current did flow all the way to the load. Define the source voltage Vsend, the feeder-end voltage Vload, and the line current at the source Iline. Then the so-called equivalent line impedance is given by

(31)

This impedance is NOT the same as the actual line impedance. The only way to obtain it is to run a power flow without the regulator and extract the three quantities of eq. (31) from the power flow solution.

16.7 Regulator settings

In addition to the load drop compensator impedance values, there are three other important regulator settings (Fig. 9 may be useful to view while reading the below):

- Set voltage: The desired output of the regulator. It is the voltage level that the regulator tries to hold, and is a setting of the voltage relay. (The voltage relay is the receiver of the intelligence from the circuit in which the regulator is located, and it initiates operation of the tap-changer).

- Bandwidth: In order to prevent continuous tap-changing, (and therefore increase the regulator life), the voltage relay does not actuate until the difference between the set and measured voltage exceeds half the bandwidth. Settings of 1.5, 2, and 2.5 volts are common for ±10%, 32 step regulators. If set voltage is 120 volts and bandwidth is 2 volts, the regulator will change taps until load voltage lies between 119-121 volts.

- Time delay: In order to prevent tap changing during a transient or short-time change in current, and therefore reduce the frequency of tap changing, a time delay relay is inserted between the voltage relay and the motor operating circuit. This is the waiting time between the time when the voltage goes out of bandwidth and when the motor operating circuit actually begins to move the tap, i.e., the length of time that a raise or lower operation is called for before actual execution of the command. Typical time delays are 30 to 60 seconds.

Fig. 11 illustrates the above 3 settings [3].

Fig. 11

Example 3:

The substation transformer of Example 2 is supplying 2500 kVA at 4.16 kV (L-L) and 0.9 pf lag. The line-drop compensator impedance was set as computed in Ex 2, i.e.,

ohms. The set voltage is 120 volts and the bandwidth is 2 volts.

Determine the regulator tap position that will hold the load center voltage at the desired voltage level and within the bandwidth.

So the tap on the regulator needs to be set so that the voltage at the load center lies between 119 and 121 volts.

Solution:

Again we assume the phases are balanced and we are designing a regulator for one of the phases.

Our approach is to compute the voltage seen by the voltage relay assuming no voltage regulator action, and then to compute the minimum number of tap changes necessary to move the voltage to either 119 (if it is below) or 121 (if it is above).

The first step is to compute the actual line current. The magnitude is given by

Since pf=0.9 lag, the current angle (assuming the L-N voltage is reference) is:

So the current phasor is:

Now this can be used to obtain the compensator current via use of the CT ratio, which is CTp/CTs=700/5=140. Therefore

The L-N voltage at the transformer low side is given by 4160/sqrt(3)=2401.8. Since we are assuming this is the reference, then it has angle of 0 degrees. Then the regulator voltage is transformer by the PT ratio, which is 2401.8:120, therefore the compensator voltage is 120 volts.

The relay voltage in the compensator circuit equals 120 volts less the drop across the compensator impedance. The drop across the compensator impedance is given by the compensator current times the compensator impedance.

The drop across the compensator impedance is:

The relay voltage is:

Now we need at least 119 volts.

Recalling from Section 16.4 that we obtain 0.00625 pu voltage per step, this will be 0.00625*120=0.75 volts/step.

Therefore we will need to move an amount of steps given by

Tap=

Now we can only take an integer number of steps, so let’s assume we take 13 steps.

From eq. (16), we can get the regulator ratio:

Example 4:

Assume that in Example 3, the 2500 kVA at 4.16 kV (L-L) and 0.9 pf lag is measured at the low side of the substation transformer terminals.

Compute the actual voltage at the load.

Solution:

Recall that we know, from Example 2, the equivalent impedance between the regulator and the load is 0.3+j0.9 ohms. Therefore if we obtain the voltage and current on the load side of the regulator, we can compute the load voltage.

To obtain the voltage and current on the load side of the regulator, we make use of the generalized constants for the regulator (see eqs. 21-24):

Applying eqs. (19-20):

But what is VS and IS? These quantities are on the source side of the regulator, which means the low side of the substation transformer. Therefore:

volts and

(see ex. 3)

Then

From this we may obtain the actual line-to-ground voltage at the load as:

On a 120 volt base, the load voltage is

16.8 Three-phase voltage regulators

Three-phase regulators may be obtained by interconnecting 3 single-phase regulators.

There are four different ways in use for connecting single phase regulators for three-phase circuit regulation. They are:

- Three regulators connected in grounded-Y.

- Three regulators connected in closed delta.

- Two regulators connected in “open-wye” (sometimes also called “V” phase)

- Two regulators connected in open delta

In all of these cases, each regulator has its own compensator circuit controlling the voltage corresponding to its corresponding voltage only. Therefore, the taps on each regulator are changed separately.

We will only discuss the most common of these, the grounded-Y configuration, which is shown in Fig. 12.

Fig. 12

The following equations may be developed for the three-phase grounded-Y regulator:

(32)

And

(33)

Equations (32-33) are in the form of

where

The above model provides that the regulator ratio for each phase may be different.

It is also possible to have all three regulators using the same phase voltages and current for input control signals in which case the 3 regulators will always be changed by the same number of taps.

Finally, there is also available and in use the so-called three-phase regulator (in contrast to three interconnected single phase regulators). The three phase regulator is gang-operated so that the taps on all windings change the same and, as a result, only one compensator circuit is required.

In either of the previous two cases, it is up to the engineer to decide which phase current and voltage will be sampled by the compensator circuit.

References

[1] A. Pansini, “Electrical distribution engineering,” McGraw-Hill, 1983.

[2] B. Lloyd, “Distribution transformers,” Chapter 6 in “Distribution Systems, Electric Utility Engineering Reference Book,” Westinghouse Corporation, 1965.

[3] T. Short, “Electric power distribution handbook,” CRC press, 2004.