Notes 21: Protection

21.0 Introduction

Distribution system protection involves using current interrupting devices to de-energize faulted portions of the network so that the associated high fault currents will not  flow.  Otherwise, continued high fault current that is not interrupted can cause significant heat, resulting in damaged equipment (e.g., line burn-downs, transformer loss of life) and in the worst case fires and explosions. In addition, faults can sometimes expose people to live conductors, resulting in a safety hazard.

In addition, the coordination of protective devices can be done in such a way so as to minimize interruptions and interruption durations as seem by customer, thus improving their overall reliability levels.

In this document, we will briefly survey the field of protection for distribution systems. This should be viewed as an introduction only. Students desiring more in-depth treatment of the subject should refer to one of the four very good references listed in the bibliography of this document.

21.1 Basic principles

Directional relays are unnecessary in radial distribution systems that do not have any distributed generation. So almost all distribution protection devices are simply non-directional, overcurrent devices. (Exceptions are, however, when the distribution system has multiple feeds and/or when it contains generation).

The four most basic requirements for an overcurrent interrupting device is that

- Do not operate for highest load current.

- Do operate for minimum fault current.

- Must be capable of interrupting the maximum fault current.

- Interrupt more severe faults more quickly.

21.1.1 Maximum load current

The load currents of concern are those highest in magnitude which therefore may appear to the protective device as a fault current. An interrupting device should obviously never open for any load current.

The highest load current is typically the current that occurs just as the system is re-energized following an outage. This current is commonly referred to as the cold-load pickup current.

The cold-load pick-up current can be significantly higher than the normal peak load current because of two main reasons.

Current in-rush: Cold-load pickup currents can be affected during the first second or so following energization by current inrush, which is the tendency of magnetic loads (e.g., transformers and motors) to draw high currents during the initial transient period as a result of the difference between the residual magnetization of the iron and the initial phase applied across the device.

Simultaneous operation: Cold-load pickup is also affected by the fact that following an outage, on re-energizing, many devices that normally do not run simultaneously will switch on instantaneously, and simultaneously. This is particularly true of devices that perform temperature control, e.g., air conditioners, furnaces, water heaters, refrigerators.

Cold-load pickup currents can range from 2-5 times normal peak load currents during the first few seconds following re-energization and [2].

21.1.2 Minimum fault current

The minimum fault current is determined by the least severe fault within the protection zone of the device.

The protection zone is defined by the reach of the device. The reach is the maximum distance from the device to a fault for which the protective device is supposed to operate.

As the fault moves further from the source, the impedance between source and fault increases and the fault current decreases.

So the reach of an overcurrent device increases as the current interruption setting decreases.

Observation: Location of the maximum distance fault depends only on the current setting and not on the device location.

So basic procedure is that one identifies the least severe fault type, computes the fault current for the maximum distance fault. This fault current is the minimum fault current and the device should be set to operate at a level

- Significantly higher than the maximum load current and

- Significantly lower than the minimum fault current

What happens when this is not possible?

Is it ever the case that it is not possible?

Fact: There always exist faulted conditions for which the fault current is less than the maximum load current!!!

How can this be?

Consider the single-line-to-ground (SLG) fault. In “notes20,” we found that the connection for a SLG fault was as in Fig. 1:

Fig. 1

Sequence fault currents are:

(1)

And the phase a fault current Ifa=3I1fa.

However, this is for a so-called bolted fault, which means that the fault is a pure short-circuit with no fault impedance.

For a SLG fault through an impedance Zf, the fault impedance shows up in all three sequence networks, so that the sequence network connection is as in Fig. 2.

Fig. 2

Then the sequence fault currents are:

(2)

Again we have that Ifa=3I1fa.

The difference between this case and the bolted fault case is that the 3Zf term is in the denominator, so that the fault current is decreased. If Zf is large, the fault current can be decreased significantly.

What can Zf be? Consider the case where an overhead conductor crossing a street breaks and falls to the pavement. In this case, the impedance between the conductor and ground is going to be very high. Then, clearly, the fault current is going to be very low.

Such a situation is quite dangerous because the protection device will not trip.

It is for this reason that a distribution substation transformer is almost never connected in ungrounded Y, because then, the zero sequence circuit is open, which is equivalent to Zf=∞, and no fault current flows!

So we see that, because of the variability of Zf, there will always be some faults that result in currents that are below the maximum load current.

Therefore, it is typical to define the minimum fault current as that which would flow for a SLG fault through a fault impedance of 30 or 40 ohms.

21.1.3 Time to operate

The heating effect of a fault current is depends on the energy dissipated. The energy dissipated depends on two things:

- Power and

- Time

Since the power is given by I2R, and since R is fixed, we see that the variable parameters for a particular faulted condition are the square of the current and the time or duration of the fault.

So I2t is an important parameter in determining the severity of a fault.

In order to protect equipment and people, protection should be designed so that it avoids exceeding a certain value of I2t.

So we see that a good design for a protection device is one that operates faster (smaller t) for higher values of current (larger I).

This thinking results in the so-called time-inverse characteristic of a protection device, shown in Fig. 3.

Fig. 3

21.2 Types of protection devices

There are four basic types of protection devices used in distribution systems. These are

- Fuses

- Automatic circuit reclosers

- Sectionalizers

- Circuit breakers and relays

We will discuss each of these briefly.

21.2.1 Fuses

Fuses have elements that melt if enough current flows through it for enough time.

They are inexpensive, and they can open very fast for high currents.

The most common type of fuse is the expulsion type within a cue out, illustrated in Fig. 4.

Fig. 4

The purpose of the cutout is to support the fuse and enable efficient replacement when it is blown. One often sees these devices.

The fuse is called expulsion because, when the fusible element, located within a fuse tube, melts under high current, an arc remains. The arc causes a rapid pressure buildup, which forces the ionized gas out of the bottom of the cutout, which helps to prevent reigniting. Fig. 5 shows operation of an expulsion fuse, which suggests that they should not be placed where a blast of hot ionized gas could cause a flashover on another phase.

Fig. 5 [2]

Industry standards specify two types of expulsion fuses.

- K type: fast fuse with speed ratio of 6-8

- T-type: slower fuse with speed ratio 10-13

The speed ratio is the ratio of

- The melting current at 0.1 second to

- The melting current at X seconds, where X is 300 for fuse ratings below 100 amps and X is 600 for fuse ratings above 100 amps.

The current rating is the level of current the fuse can safely carry for an indefinite period of time.

For example, a typical K-type fuse would have ratio (using 600 seconds) of 200/30=6.7.

21.2.2 Circuit breakers and relays

21.2.3 Automatic circuit reclosers

ACRs are essentially circuit breakers with increased capacity both in terms of interrupting capacity and normal load carrying capacity.

They are less expensive than circuit breakers but less accurate.

ACRs are motivated by the fact that 60-80% of all overhead distribution faults are temporary and last only a few cycles or a few seconds. For example, a branch may blow against a circuit and then fall to the ground.

As a result, it becomes very attractive to reclose following an initial opening of the protection device.

So the basic operation of an ACR is to

- Sense the overcurrent

- Time and interrupt the overcurrent

- Reclose to re-energize the circuit

An ACR can reclose as many as 3-4 times before “locking out.”

The first reclose is generally done “instantaneously” which means there is no intentional time delay embedded in the first reclose. Typical timing sequences used in the industry include

- 0-15-30 seconds

- 0-30-60-90 seconds

- 5-45 seconds

But most ACRs can be set for any combination  of  instantaneous operations or time delayed operations.

21.2.4 Sectionalizers

Sectionalizers are switches. The main difference between a switch an all other devices described previously is that all the other devices can detect and interrupt a short-circuit fault current, but a switch  can do neither.

It is typically applied together with an ACR or a circuit breaker to isolate faulted sections of the distribution system.

So how does a sectionalizer operate?

- It counts the number of operations of the “backup” device

- After a pre-set number of interruptions, it opens while the backup device is open.

- Then the backup device can reclose to restore service to remaining circuits.

Advantage relative to fuse is it is unnecessary to replace it.

Advantage relative to circuit breaker or ACR is it is less expensive.

Clear disadvantage is that it is a switch.

21.3 Coordination

The basic issue in coordinating multiple devices in a distribution feeder is that we want to ensure that only the minimum number of customers are interrupted for a specific fault, given the devices that we have in place.

We use the terms “protected device” (upstream) and “protecting device” (downstream).

Important coordinating principles:

- The protecting device must clear a fault before the protected device interrupts the circuit (fuse) or operates to lockout.

- Outages caused by permanent faults must be restricted to the smallest section of the system for the shortest time.

Figure 6 shows an example of system coordination  where a substation receives power flow a high voltage transmission line and steps the voltage down.

Protective devices in this illustration are located at the coordinating points. Device A is at the substation. Devices C and H are in the feeder. Device B is at the branch tap off the feeder.

Device D is on the transformer primary and devices E, F, and G are service entrance fuses on the transformer secondary. All devices must be selected to carry normal load current and respond properly to a fault.

Fig. 6 [1]

With respect to device H, device C is the protected device. For a fault at point 1, device C must not open and device H must interrupt.

With respect to device A, device C is the protecting device and must interrupt permanent fault current at point 2 before device A operates to lockout. Device B is also a protecting device for A and must operate similar to device C for a fault at point 3. Only device A functions when a fault occurs between A and C, such as at point 4. For a transformer fault at point 5, device D is expected to interrupt current and permit normal load current to flow in the remainder of the system. For an overload on the secondary tap of transformer at point 6, device E should interrupt the circuit, permitting power to the transformer to be continued so that customers on other secondary taps will receive service.

References

[1] McGraw-Edison Power Systems, “Distribution system protection manual.”

[2] T. Short, “Electric power distribution handbook,” CRC press, 2004.

[3] T. Gonen, “Electric Power Distribution System Engineering,” McGraw-Hill, 1986.

[4] J. Blackburn and G. Rockefeller, “Applied Protective Relaying,” Westinghouse Corporation.

[5] J. Blackburn, “Protective Relaying: Principles and Applications,” 2nd edition, Marcel-Dekker, New York, 1998.

[6] P. Anderson, “Power system protection,” McGraw-Hill, 1999.